## locations
dbo.section | dbo.entity_name | dbo.type | dbo.id | dbo.connections.contains
Buildings | UK-LON-BLDNG1 | FACILITIES/BUILDING | 3654fc48-914e-4a55-82f6-126534244886
Floors | UK-LON-BLDNG1_FL1 | FACILITIES/FLOOR | a388563d-58e3-4534-b133-19389f6650a4 | UK-LON-KGX1
Rooms | UK-LON-BLDNG1_RM1 | FACILITIES/ROOM | b9f2c8b8-d67e-4b50-824a-7b48ff877429 | UK-LON-BLDNG1-FL1
Zones | UK-LON-BLDNG1_ZN1 | HVAC/ZONE | a0f68db4-f074-49cf-8e80-d65634587f9f | UK-LON-BLDNG1-RM1
Rooms | UK-LON-BLDNG1_RM2 | FACILITIES/ROOM | 58d709a5-aa50-4134-a035-0ccc2d01fd48 | UK-LON-BLDNG1_FL1
Zones | UK-LON-BLDNG1_ZN2 | HVAC/ZONE | bdf2e667-8ab2-4ae3-bcc9-9c6c7d995535 | UK-LON-BLDNG1_RM2

## assets
entity_instance_name | udmi.version | udmi.timestamp | udmi.system.location.site | udmi.system.location.section | udmi.system.location.position.x | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.pointset.points | udmi.cloud.auth_type | dbo.devices_or_virtual_devices | dbo.type | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | Location | Reporting Device
AHU-24 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/AHU_CHWSC_HWSC_ | ZONE-RB2-024 | VSD-84, VSD-85 | AHU-24_1, AHU-24_2, AHU-24_3, VSD-84, VSD-85 | ahu-24 | RB2-024 | BMS-58, BMS-158, Server, VSD-84, VSD-85
AHU-241 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM1 | 10 | 10 | 10 | 3lo6v$zmnD_9mhr2e9HJst | UK-LON-BLDNG1 | AHU-241 | ahu-24_1 | RS256 | Device | HVAC/AHU_ |  |  |  |  | RB2-024 | BMS-58
AHU-242 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM1 | 10 | 10 | 10 | 26rmarOMz9ZOgBkt9da8MC | UK-LON-BLDNG1 | AHU-242 | ahu-24_2 | RS256 | Device | HVAC/AHU_ |  | DMP-1, DMP-2, DMP-3, DMP-4 |  |  | RB2-024 | BMS-158
AHU-243 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM1 | 10 | 10 | 10 |  | UK-LON-BLDNG1 | AHU-243 | ahu-24_3 | RS256 | Device | HVAC/AHU_ | [5 empty] | Server
DMP-1 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/DMP_PDSCV | AHU-24 |  | AHU-24_2 | dmp-ahu-sa-1 | RB2-024 | BMS-158
DMP-2 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/DMP_ |  |  | AHU-24_2 | dmp-ahu-ea-1 | RB2-024 | BMS-158
DMP-3 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/DMP_PDSCV | AHU-24 |  | AHU-24_2 | dmp-ahu-sa-2 | RB2-024 | BMS-158
DMP-4 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/DMP_ |  |  | AHU-24_2 | dmp-ahu-ea-2 | RB2-024 | BMS-158
MTR-49 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | 16H1aL4AP5qvjYZedFS7_9 |  |  |  |  | Virtual | HVAC/MTR_ |  |  | AHU-24_1 | mtr-ahu-cw | RB2-024 | BMS-58
MTR-50 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | 16H1aL4AP5qvjYZedFS7_B |  |  |  |  | Virtual | HVAC/MTR_ |  |  | AHU-24_1 | mtr-ahu-hw | RB2-024 | BMS-58
VSD-84 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM1 | 10 | 10 | 10 | 1RMH3pjGXADB5SUTsnch8y | UK-LON-BLDNG1 | VSD-84 | vsd-sf1 | RS256 | Device | HVAC/VSD_PDSCV_ |  |  |  |  | RB2-024 | VSD-84
VSD-85 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM1 | 10 | 10 | 10 | 1RMH3pjGXADB5SUTsnch8$ | UK-LON-BLDNG1 | VSD-85 | vsd-ef1 | RS256 | Device | HVAC/VSD_EDPM_ |  |  |  |  | RB2-024 | VSD-85
AHU-11 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 |  | 10 | 10 | 10 | [5 empty] | Virtual | HVAC/AHU_ | ZONE-RB2-043 | VSD-60 | AHU-11_1, AHU-11_2, VSD-60 | ahu-11 | RB2-043 | BMS-45, Server, VSD-60
AHU-111 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM2 | 10 | 10 | 10 | a0e5c80f-73d2-428f-939c-2283b6c945e9 | UK-LON-BLDNG1 | AHU-111 | ahu-11_1 | RS256 | Device | HVAC/AHU_ |  |  |  |  | RB2-043 | BMS-45
AHU-112 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM2 | 10 | 10 | 10 |  | UK-LON-BLDNG1 | AHU-112 | ahu-11_2 | RS256 | Device | HVAC/AHU_ |  |  |  |  | RB2-043 | Server
VSD-60 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM2 | 10 | 10 | 10 |  | UK-LON-BLDNG1 | VSD-60 | vsd-sf2 | RS256 | Device | HVAC/VSD_ |  |  |  |  | RB2-043 | VSD-60
MTR-25 | 1 | 2020-12-08T09:03:43Z | UK-LON-BLDNG1 | UK-LON-BLDNG1_RM2 | 10 | 10 | 10 |  | UK-LON-BLDNG1 | MTR-25 | mtr-ahu-cw | RS256 | Device | HVAC/MTR_ |  |  |  |  | RB2-043 | BMS-45

## device_entities
points_type | udmi.pointset.points | udmi.pointset.units | dbo.states | dbo.translation.fields | dbo.translation.units | dbo.abstracts
ahu-24_1 | mixed_air_temperature_sensor | Degrees-Celsius |  | mixed_air_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | mixed_air_humidity_sensor | Percent-relative-humidity |  | mixed_air_relative_humidity_sensor | percent_relative_humidity: "%RH"
ahu-24_1 | leaving_cooling_coil_temperature_sensor | Degrees-Celsius |  | leaving_cooling_coil_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | leaving_cooling_coil_humidity_sensor | Percent-relative-humidity |  | leaving_cooling_coil_humidity_sensor | percent_relative_humidity: "%RH"
ahu-24_1 | supply_air_temperature_sensor | Degrees-Celsius |  | supply_air_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | supply_air_humidity_sensor | Percent-relative-humidity |  | supply_air_relative_humidity_sensor | percent_relative_humidity: "%RH"
ahu-24_1 | return_air_temperature_sensor | Degrees-Celsius |  | return_air_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | return_air_relative_humidity_sensor | Percent-relative-humidity |  | return_air_relative_humidity_sensor | percent_relative_humidity: "%RH"
ahu-24_1 | extract_air_co2_concentration_sensor | Parts-per-million |  | exhaust_air_co2_concentration_sensor | parts_per_million: "PPM"
ahu-24_1 | hygroscopic_wheel_alarm_status | No-units | true=ALARM false=HEALTHY | hygroscopic_wheel_alarm_status
ahu-24_1 | fire_alarm_status | No-units | true=ALARM false=HEALTHY | fire_alarm_status
ahu-24_1 | cooling_valve_percentage_command | Percent |  | chilled_water_valve_percentage_command | percent: "%"
ahu-24_1 | heating_valve_percentage_command | Percent |  | heating_water_valve_percentage_command | percent: "%"
ahu-24_1 | hygroscopic_wheel_speed_command | Percent |  | hygroscopic_wheel_speed_command | percent: "%"
ahu-24_1 | cooling_water_flowrate_sensor | Liters-per-second |  | chilled_water_flowrate_sensor | liters_per_second: "L/s"
ahu-24_1 | entering_cooling_coil_temperature_sensor | Degrees-Celsius |  | entering_cooling_coil_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | cooling_coil_differential_temperature_sensor | Degrees-Celsius |  | cooling_coil_differential_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | cooling_coil_energy_sensor | Kilojoules |  | cooling_coil_energy_sensor | kilojoules: "kJ"
ahu-24_1 | heating_water_flowrate_sensor | Liters-per-second |  | heating_water_flowrate_sensor | liters_per_second: "L/s"
ahu-24_1 | entering_heating_coil_temperature_sensor | Degrees-Celsius |  | entering_heating_coil_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | leaving_heating_coil_temperature_sensor | Degrees-Celsius |  | leaving_heating_coil_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | heating_coil_differential_temperature_sensor | Degrees-Celsius |  | heating_coil_differential_temperature_sensor | degrees_celsius: "degC"
ahu-24_1 | heating_coil_energy_sensor | Kilojoules |  | heating_coil_energy_sensor | kilojoules: "kJ"
ahu-24_1 | supply_air_pid_gain_temperature_setpoint | No-units |  | supply_air_pid_gain_temperature_setpoint | no_units: "no_units"
ahu-24_1 | supply_air_pid_integral_temperature_setpoint | Minutes |  | supply_air_pid_integral_temperature_setpoint | minutes: "min"
ahu-24_1 | supply_air_pid_derivative_temperature_setpoint | Minutes |  | supply_air_pid_derivative_temperature_setpoint | minutes: "min"
ahu-24_1 | supply_air_pid_gain_moisture_setpoint | No-units |  | supply_air_pid_gain_moisture_setpoint | no_units: "no_units"
ahu-24_1 | supply_air_pid_integral_moisture_setpoint | Minutes |  | supply_air_pid_integral_moisture_setpoint | minutes: "min"
ahu-24_1 | supply_air_pid_derivative_moisture_setpoint | Minutes |  | supply_air_pid_derivative_moisture_setpoint | minutes: "min"
ahu-24_1 | return_air_co2_pid_gain_concentration_setpoint | No-units |  | return_air_co2_pid_gain_concentration_setpoint | no_units: "no_units"
ahu-24_1 | return_air_co2_pid_integral_concentration_setpoint | Minutes |  | return_air_co2_pid_integral_concentration_setpoint | minutes: "min"
ahu-24_1 | return_air_co2_pid_derivative_concentration_setpoint | Minutes |  | return_air_co2_pid_derivative_concentration_setpoint | minutes: "min"
ahu-24_2 | supply_air_damper_percentage_sensor_1 | Percent |  | supply_air_damper_percentage_sensor_1 | percent: "%"
ahu-24_2 | extract_air_damper_percentage_sensor_1 | Percent |  | exhaust_air_damper_percentage_sensor_1 | percent: "%"
ahu-24_2 | supply_air_damper_percentage_sensor_2 | Percent |  | supply_air_damper_percentage_sensor_2 | percent: "%"
ahu-24_2 | extract_air_damper_percentage_sensor_2 | Percent |  | exhaust_air_damper_percentage_sensor_2 | percent: "%"
ahu-24_2 | extract_air_co2_concentration_sensor | Parts-per-million |  | exhaust_air_co2_concentration_sensor_2 | parts_per_million: "PPM"
ahu-24_2 | extract_air_co2_concentration_sensor_1 | Parts-per-million |  | exhaust_air_co2_concentration_sensor_1 | parts_per_million: "PPM"
ahu-24_2 | supply_air_damper_percentage_command_1 | Percent |  | supply_air_damper_percentage_command_1 | percent: "%"
ahu-24_2 | extract_air_damper_percentage_command_1 | Percent |  | exhaust_air_damper_percentage_command_1 | percent: "%"
ahu-24_2 | supply_air_damper_percentage_command_2 | Percent |  | supply_air_damper_percentage_command_2 | percent: "%"
ahu-24_2 | extract_air_damper_percentage_command_2 | Percent |  | exhaust_air_damper_percentage_command_2 | percent: "%"
ahu-24_2 | return_air_co2_concentration_setpoint | Parts-per-million |  | return_air_co2_concentration_setpoint | parts_per_million: "PPM"
ahu-24_2 | return_air_co2_pid_gain_concentration_setpoint | No-units |  | return_air_co2_pid_gain_concentration_setpoint | no_units: "no_units"
ahu-24_2 | return_air_co2_pid_integral_concentration_setpoint | Minutes |  | return_air_co2_pid_integral_concentration_setpoint | minutes: "min"
ahu-24_2 | return_air_co2_pid_derivative_concentration_setpoint | Minutes |  | return_air_co2_pid_derivative_concentration_setpoint | minutes: "min"
ahu-24_3 | inlet_damper_alarm_status | No-units | true=ALARM false=HEALTHY | supply_air_damper_alarm_status
ahu-24_3 | mixing_damper_alarm_status | No-units | true=ALARM false=HEALTHY | mixing_air_damper_alarm_status
ahu-24_3 | extract_damper_alarm_status | No-units | true=ALARM false=HEALTHY | exhaust_air_damper_alarm_status
ahu-24_3 | supply_fan_volume_sensor | Cubic-meters |  | supply_air_volume_sensor | cubic_meters: "m3"
ahu-24_3 | extract_fan_volume_sensor | Cubic-meters |  | exhaust_fan_volume_sensor | cubic_meters: "m3"
ahu-24_3 | supply_fan_demand_status | No-units | true=DEMAND false=NO_DEMAND | supply_fan_demand_status
ahu-24_3 | extract_fan_demand_status | No-units | true=DEMAND false=NO_DEMAND | exhaust_fan_demand_status
ahu-24_3 | outside_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | outside_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | return_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | return_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | cooling_air_moisture_sensor | BTUs-per-pound-dry-air |  | cooling_air_moisture_sensor | btus_per_pound_dry_air: "Btu/lb"
ahu-24_3 | cooling_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | cooling_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | heating_air_moisture_sensor | BTUs-per-pound-dry-air |  | heating_air_moisture_sensor | btus_per_pound_dry_air: "Btu/lb"
ahu-24_3 | heating_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | heating_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | return_air_moisture_sensor | BTUs-per-pound-dry-air |  | return_air_moisture_sensor | btus_per_pound_dry_air: "Btu/lb"
ahu-24_3 | return_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | return_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | mixed_air_moisture_sensor | BTUs-per-pound-dry-air |  | mixed_air_moisture_sensor | btus_per_pound_dry_air: "Btu/lb"
ahu-24_3 | mixed_air_enthalpy_sensor | Joules-per-kilogram-dry-air |  | mixed_air_enthalpy_sensor | joules_per_kilogram: "J/kg"
ahu-24_3 | supply_air_temperature_setpoint | Degrees-Celsius |  | supply_air_temperature_setpoint | degrees_celsius: "degC"
ahu-24_3 | supply_air_moisture_setpoint | BTUs-per-pound-dry-air |  | supply_air_moisture_setpoint | btus_per_pound_dry_air: "Btu/lb"
ahu-24_3 | return_air_co2_concentration_setpoint | Parts-per-million |  | return_air_co2_concentration_setpoint | parts_per_million: "PPM"
ahu-24_3 | min_inlet_damper_percentage_setpoint | Percent |  | min_supply_air_damper_percentage_setpoint | percent: "%"
ahu-24_3 | mixing_damper_offset_percentage_setpoint | Percent |  | mixing_air_damper_offset_percentage_setpoint | percent: "%"
ahu-24_3 | carbon_filter_period_setpoint | Hours |  | carbon_filter_period_setpoint | hours: "Hrs"
ahu-24_3 | hygroscopic_wheel_period_setpoint | Minutes |  | hygroscopic_wheel_period_setpoint | minutes: "min"
ahu-24_3 | extract_fan_offset_percentage_setpoint | Percent |  | exhaust_fan_offset_percentage_setpoint | percent: "%"
ahu-24_3 | heating_valve_demand_percentage_setpoint | Percent |  | heating_water_valve_demand_percentage_setpoint | percent: "%"
ahu-24_3 | cooling_valve_demand_percentage_setpoint | Percent |  | chilled_water_valve_demand_percentage_setpoint | percent: "%"
vsd-sf1 | safety_interlock | No-units | true=ON false=OFF | safety_interlock
vsd-sf1 | supply_damper_percentage_sensor | Percent |  | supply_air_damper_percentage_sensor | percent: "%" | PDSCV
vsd-sf1 | mixing_damper_percentage_sensor | Percent |  | mixing_air_damper_percentage_sensor | percent: "%"
vsd-sf1 | supply_damper_percentage_command | Percent |  | supply_air_damper_percentage_command | percent: "%" | PDSCV
vsd-sf1 | mixing_damper_percentage_command | Percent |  | mixing_air_damper_percentage_command | percent: "%"
vsd-sf1 | supply_panel_filter_differential_pressure_sensor | Pascals |  | supply_panel_filter_differential_pressure_sensor | pascals: "Pa"
vsd-sf1 | supply_air_pressure_sensor | Pascals |  | supply_air_pressure_sensor | pascals: "Pa"
vsd-sf1 | supply_fan_run_status | No-units | true=RUNNING false=NOT_RUNNING | supply_fan_run_status
vsd-sf1 | supply_fan_fault_status | No-units | true=FAULT false=HEALTHY | supply_fan_fault_status
vsd-sf1 | supply_air_high_pressure_status | No-units | true=ALARM false=HEALTHY | supply_air_high_pressure_status
vsd-sf1 | supply_fan_speed_percentage_sensor | Hertz |  | supply_fan_speed_frequency_sensor | hertz: "Hz"
vsd-sf1 | supply_fan_alarm_status | No-units | true=ALARM false=HEALTHY | supply_fan_alarm_status
vsd-sf1 | supply_fan_auto_status | No-units | true=AUTO false=OUT_OF_AUTO | supply_fan_auto_status
vsd-sf1 | supply_fan_power_sensor | Kilowatts |  | supply_fan_power_sensor | kilowatts: "kW"
vsd-sf1 | supply_fan_energy_sensor | Kilowatt-hours |  | supply_fan_energy_sensor | kilowatt_hours: "kW-hrs"
vsd-sf1 | supply_fan_current_sensor | Amperes |  | supply_fan_current_sensor | amperes: "A"
vsd-sf1 | supply_fan_voltage_sensor | Volts |  | supply_fan_voltage_sensor | volts: "V"
vsd-sf1 | supply_fan_run_period_sensor | Hours |  | supply_fan_run_period_sensor | hours: "Hrs"
vsd-sf1 | drive_dc_voltage_sensor | Volts |  | drive_dc_voltage_sensor | volts: "V"
vsd-sf1 | thermal_overload_percentage_sensor | Percent |  | thermal_overload_percentage_sensor | percent: "%"
vsd-sf1 | thermal_overload_alarm_status | No-units | true=ALARM false=HEALTHY | thermal_overload_alarm_status
vsd-sf1 | heatsync_temperature_sensor | Degrees-Celsius |  | heatsync_temperature_sensor | degrees_celsius: "degC"
vsd-sf1 | supply_air_high_pressure_setpoint | Pascals |  | supply_air_high_pressure_setpoint | pascals: "Pa"
vsd-sf1 | supply_air_pressure_setpoint | Pascals |  | supply_air_pressure_setpoint | pascals: "Pa"
vsd-ef1 | exhaust_damper_percentage_sensor | Percent |  | exhaust_air_damper_percentage_sensor | percent: "%" | EDPM
vsd-ef1 | exhaust_damper_percentage_command | Percent |  | exhaust_air_damper_percentage_command | percent: "%" | EDPM
vsd-ef1 | safety_interlock | No-units | true=ON false=OFF | safety_interlock
vsd-ef1 | extract_panel_filter_differential_pressure_sensor | Pascals |  | exhaust_panel_filter_differential_pressure_sensor | pascals: "Pa"
vsd-ef1 | supply_bag_filter_differential_pressure_sensor | Pascals |  | supply_bag_filter_differential_pressure_sensor | pascals: "Pa"
vsd-ef1 | extract_air_pressure_sensor | Pascals |  | exhaust_air_pressure_sensor | pascals: "Pa"
vsd-ef1 | extract_fan_volume_sensor | Pascals |  | exhaust_fan_volume_sensor | pascals: "Pa"
vsd-ef1 | extract_fan_run_status | No-units | true=RUNNING false=NOT_RUNNING | exhaust_fan_run_status
vsd-ef1 | extract_fan_fault_status | No-units | true=FAULT false=HEALTHY | exhaust_fan_fault_status
vsd-ef1 | extract_air_low_pressure_status | No-units | true=ALARM false=HEALTHY | exhaust_air_low_pressure_status
vsd-ef1 | extract_fan_speed_percentage_sensor | Hertz |  | exhaust_fan_speed_frequency_sensor | hertz: "Hz"
vsd-ef1 | extract_fan_alarm_status | No-units | true=ALARM false=HEALTHY | exhaust_fan_alarm_status
vsd-ef1 | extract_fan_auto_status | No-units | true=AUTO false=OUT_OF_AUTO | exhaust_fan_auto_status
vsd-ef1 | extract_fan_power_sensor | Kilowatts |  | exhaust_fan_power_sensor | kilowatts: "kW"
vsd-ef1 | extract_fan_energy_sensor | Kilowatt-hours |  | exhaust_fan_energy_sensor | kilowatt_hours: "kW-hrs"
vsd-ef1 | extract_fan_current_sensor | Amperes |  | exhaust_fan_current_sensor | amperes: "A"
vsd-ef1 | extract_fan_voltage_sensor | Volts |  | exhaust_fan_voltage_sensor | volts: "V"
vsd-ef1 | extract_fan_run_period_sensor | Hours |  | exhaust_fan_run_period_sensor | hours: "Hrs"
vsd-ef1 | drive_dc_voltage_sensor | Volts |  | drive_dc_voltage_sensor | volts: "V"
vsd-ef1 | thermal_overload_percentage_sensor | Percent |  | thermal_overload_percentage_sensor | percent: "%"
vsd-ef1 | thermal_overload_alarm_status | No-units | true=ALARM false=HEALTHY | thermal_overload_alarm_status
vsd-ef1 | heatsync_temperature_sensor | Degrees-Celsius |  | heatsync_temperature_sensor | degrees_celsius: "degC"
vsd-ef1 | extract_air_low_pressure_setpoint | Pascals |  | exhaust_air_low_pressure_setpoint | pascals: "Pa"
ahu-11_1 | supply_air_temperature_sensor | Degrees-Celsius |  | supply_air_temperature_sensor | degrees_celsius: "degC" | STM | Existing
ahu-11_1 | zone_air_temperature_sensor | Degrees-Celsius |  | zone_air_temperature_sensor | degrees_celsius: "degC" | ZTM, ZTC, CHWZTC | Existing
ahu-11_1 | fire_alarm_status | No-units | true=ALARM false=HEALTHY | fire_alarm_status |  |  | New Field & Abstract Required
ahu-11_1 | cooling_valve_percentage_command | Percent |  | chilled_water_valve_percentage_command | percent: "%" | CHWZTC | Existing
ahu-11_1 | entering_cooling_coil_temperature_sensor | Degrees-Celsius |  | entering_cooling_coil_temperature_sensor | degrees_celsius: "degC" |  | New Field & Abstract Required
ahu-11_1 | leaving_cooling_coil_temperature_sensor | Degrees-Celsius |  | leaving_cooling_coil_temperature_sensor | degrees_celsius: "degC" | CHWZTC | Existing
ahu-11_1 | cooling_coil_differential_temperature_sensor | Degrees-Celsius |  | cooling_coil_differential_temperature_sensor | degrees_celsius: "degC" |  | New Field & Abstract Required
ahu-11_1 | zone_air_pid_integral_temperature_setpoint | Minutes |  | zone_air_pid_integral_temperature_setpoint | minutes: "min" |  | New Subfields, Field & Abstract Required
ahu-11_1 | zone_air_pid_derivative_temperature_setpoint | Minutes |  | zone_air_pid_derivative_temperature_setpoint | minutes: "min" |  | New Subfields, Field & Abstract Required
ahu-11_1 | zone_air_temperature_setpoint | Degrees-Celsius |  | zone_air_temperature_setpoint | degrees_celsius: "degC" | ZTC, CHWZTC | Existing
ahu-11_2 | inlet_damper_alarm_status | No-units | true=ALARM false=HEALTHY | supply_air_damper_alarm_status |  |  | New Field & Abstract Required
ahu-11_2 | supply_fan_volume_sensor | Cubic-meters |  | supply_air_volume_sensor | cubic_meters: "m3" |  | New Field & Abstract Required
ahu-11_2 | supply_fan_demand_status | No-units | true=DEMAND false=NO_DEMAND | supply_fan_demand_status |  |  | New Subfield, Field & Abstract Required
ahu-11_2 | zone_air_pid_gain_temperature_setpoint | No-units |  | zone_air_pid_gain_temperature_setpoint |  |  | New Subfields, Field & Abstract Required
ahu-11_2 | extract_fan_offset_percentage_setpoint | Percent |  | exhaust_fan_offset_percentage_setpoint | percent: "%" |  | New Subfield, Field & Abstract Required
ahu-11_2 | cooling_valve_demand_percentage_setpoint | Percent |  | chilled_water_valve_demand_percentage_setpoint | percent: "%" |  | New Subfield, Field & Abstract Required
vsd-sf2 | supply_damper_percentage_sensor | Percent |  | supply_air_damper_percentage_sensor | percent: "%"
vsd-sf2 | supply_damper_percentage_command | Percent |  | supply_air_damper_percentage_command | percent: "%"
vsd-sf2 | safety_interlock | No-units | true=ON false=OFF | safety_interlock |  |  | New Subfields, Field & Abstract Required
vsd-sf2 | supply_bag_filter_differential_pressure_sensor | Pascals |  | supply_bag_filter_differential_pressure_sensor | pascals: "Pa"
vsd-sf2 | supply_air_pressure_sensor | Pascals |  | supply_air_pressure_sensor | pascals: "Pa"
vsd-sf2 | supply_fan_run_status | No-units | true=RUNNING false=NOT_RUNNING | supply_fan_run_status
vsd-sf2 | supply_fan_fault_status | No-units | true=FAULT false=HEALTHY | supply_fan_fault_status
vsd-sf2 | supply_air_high_pressure_status | No-units | true=ALARM false=HEALTHY | supply_air_high_pressure_status
vsd-sf2 | supply_fan_speed_percentage_sensor | Hertz |  | supply_fan_speed_frequency_sensor | hertz: "Hz"
vsd-sf2 | supply_fan_alarm_status | No-units | true=ALARM false=HEALTHY | supply_fan_alarm_status
vsd-sf2 | supply_fan_auto_status | No-units | true=AUTO false=OUT_OF_AUTO | supply_fan_auto_status
vsd-sf2 | supply_fan_power_sensor | Kilowatts |  | supply_fan_power_sensor | kilowatts: "kW"
vsd-sf2 | supply_fan_energy_sensor | Kilowatt-hours |  | supply_fan_energy_sensor | kilowatt_hours: "kW-hrs"
vsd-sf2 | supply_fan_current_sensor | Amperes |  | supply_fan_current_sensor | amperes: "A"
vsd-sf2 | supply_fan_voltage_sensor | Volts |  | supply_fan_voltage_sensor | volts: "V"
vsd-sf2 | supply_fan_run_period_sensor | Hours |  | supply_fan_run_period_sensor | hours: "Hrs"
vsd-sf2 | drive_dc_voltage_sensor | Volts |  | drive_dc_voltage_sensor | volts: "V"
vsd-sf2 | thermal_overload_percentage_sensor | Percent |  | thermal_overload_percentage_sensor | percent: "%"
vsd-sf2 | thermal_overload_alarm_status | No-units | true=ALARM false=HEALTHY | thermal_overload_alarm_status
vsd-sf2 | heatsync_temperature_sensor | Degrees-Celsius |  | heatsync_temperature_sensor | degrees_celsius: "degC"
vsd-sf2 | supply_air_high_pressure_setpoint | Pascals |  | supply_air_high_pressure_setpoint | pascals: "Pa"
mtr-ahu-cw | cooling_water_flowrate_sensor | Liters-per-second |  | chilled_water_flowrate_sensor | liters_per_second: "L/s" | CHWFRM | Existing
mtr-ahu-cw | cooling_coil_energy_sensor | Kilojoules |  | cooling_coil_energy_sensor | kilojoules: "kJ" |  | New Abstract Required

## virtual_device_entities
virtual_points_type | device_points_type | dbo.source_device_field | dbo.virtual_device_field | dbo.abstracts
ahu-24 | ahu-24_1 | mixed_air_temperature_sensor | mixed_air_temperature_sensor
ahu-24 | ahu-24_1 | mixed_air_relative_humidity_sensor | mixed_air_relative_humidity_sensor
ahu-24 | ahu-24_1 | leaving_cooling_coil_temperature_sensor | leaving_cooling_coil_temperature_sensor
ahu-24 | ahu-24_1 | leaving_cooling_coil_humidity_sensor | leaving_cooling_coil_humidity_sensor
ahu-24 | ahu-24_1 | supply_air_temperature_sensor | supply_air_temperature_sensor | CHWSC, HWSC
ahu-24 | ahu-24_1 | supply_air_relative_humidity_sensor | supply_air_relative_humidity_sensor
ahu-24 | ahu-24_1 | return_air_temperature_sensor | return_air_temperature_sensor
ahu-24 | ahu-24_1 | return_air_relative_humidity_sensor | return_air_relative_humidity_sensor
ahu-24 | ahu-24_1 | exhaust_air_co2_concentration_sensor | exhaust_air_co2_concentration_sensor
ahu-24 | ahu-24_1 | hygroscopic_wheel_alarm_status | hygroscopic_wheel_alarm_status
ahu-24 | ahu-24_1 | fire_alarm_status | fire_alarm_status
ahu-24 | ahu-24_1 | chilled_water_valve_percentage_command | chilled_water_valve_percentage_command | CHWSC
ahu-24 | ahu-24_1 | heating_water_valve_percentage_command | heating_water_valve_percentage_command | HWSC
ahu-24 | ahu-24_1 | hygroscopic_wheel_speed_command | hygroscopic_wheel_speed_command
ahu-24 | ahu-24_1 | chilled_water_flowrate_sensor | chilled_water_flowrate_sensor
ahu-24 | ahu-24_1 | entering_cooling_coil_temperature_sensor | entering_cooling_coil_temperature_sensor
ahu-24 | ahu-24_1 | cooling_coil_differential_temperature_sensor | cooling_coil_differential_temperature_sensor
ahu-24 | ahu-24_1 | cooling_coil_energy_sensor | cooling_coil_energy_sensor
ahu-24 | ahu-24_1 | heating_water_flowrate_sensor | heating_water_flowrate_sensor
ahu-24 | ahu-24_1 | entering_heating_coil_temperature_sensor | entering_heating_coil_temperature_sensor
ahu-24 | ahu-24_1 | leaving_heating_coil_temperature_sensor | leaving_heating_coil_temperature_sensor
ahu-24 | ahu-24_1 | heating_coil_differential_temperature_sensor | heating_coil_differential_temperature_sensor
ahu-24 | ahu-24_1 | heating_coil_energy_sensor | heating_coil_energy_sensor
ahu-24 | ahu-24_1 | supply_air_pid_gain_temperature_setpoint | supply_air_pid_gain_temperature_setpoint
ahu-24 | ahu-24_1 | supply_air_pid_integral_temperature_setpoint | supply_air_pid_integral_temperature_setpoint
ahu-24 | ahu-24_1 | supply_air_pid_derivative_temperature_setpoint | supply_air_pid_derivative_temperature_setpoint
ahu-24 | ahu-24_1 | supply_air_pid_gain_moisture_setpoint | supply_air_pid_gain_moisture_setpoint
ahu-24 | ahu-24_1 | supply_air_pid_integral_moisture_setpoint | supply_air_pid_integral_moisture_setpoint
ahu-24 | ahu-24_1 | supply_air_pid_derivative_moisture_setpoint | supply_air_pid_derivative_moisture_setpoint
ahu-24 | ahu-24_1 | return_air_co2_pid_gain_concentration_setpoint | return_air_co2_pid_gain_concentration_setpoint
ahu-24 | ahu-24_1 | return_air_co2_pid_integral_concentration_setpoint | return_air_co2_pid_integral_concentration_setpoint
ahu-24 | ahu-24_1 | return_air_co2_pid_derivative_concentration_setpoint | return_air_co2_pid_derivative_concentration_setpoint
ahu-24 | ahu-24_2 | return_air_co2_concentration_setpoint | return_air_co2_concentration_setpoint
ahu-24 | ahu-24_3 | supply_air_damper_alarm_status | supply_air_damper_alarm_status
ahu-24 | ahu-24_3 | mixing_air_damper_alarm_status | mixing_air_damper_alarm_status
ahu-24 | ahu-24_3 | exhaust_air_damper_alarm_status | exhaust_air_damper_alarm_status
ahu-24 | ahu-24_3 | supply_air_volume_sensor | supply_air_volume_sensor
ahu-24 | ahu-24_3 | exhaust_fan_volume_sensor | exhaust_fan_volume_sensor
ahu-24 | ahu-24_3 | supply_fan_demand_status | supply_fan_demand_status
ahu-24 | ahu-24_3 | exhaust_fan_demand_status | exhaust_fan_demand_status
ahu-24 | ahu-24_3 | outside_air_enthalpy_sensor | outside_air_enthalpy_sensor
ahu-24 | ahu-24_3 | return_air_enthalpy_sensor | return_air_enthalpy_sensor
ahu-24 | ahu-24_3 | cooling_air_moisture_sensor | cooling_air_moisture_sensor
ahu-24 | ahu-24_3 | cooling_air_enthalpy_sensor | cooling_air_enthalpy_sensor
ahu-24 | ahu-24_3 | heating_air_moisture_sensor | heating_air_moisture_sensor
ahu-24 | ahu-24_3 | heating_air_enthalpy_sensor | heating_air_enthalpy_sensor
ahu-24 | ahu-24_3 | return_air_moisture_sensor | return_air_moisture_sensor
ahu-24 | ahu-24_3 | mixed_air_moisture_sensor | mixed_air_moisture_sensor
ahu-24 | ahu-24_3 | mixed_air_enthalpy_sensor | mixed_air_enthalpy_sensor
ahu-24 | ahu-24_3 | supply_air_temperature_setpoint | supply_air_temperature_setpoint | CHWSC, HWSC
ahu-24 | ahu-24_3 | supply_air_moisture_setpoint | supply_air_moisture_setpoint
ahu-24 | ahu-24_3 | min_supply_air_damper_percentage_setpoint | min_supply_air_damper_percentage_setpoint
ahu-24 | ahu-24_3 | mixing_air_damper_offset_percentage_setpoint | mixing_air_damper_offset_percentage_setpoint
ahu-24 | ahu-24_3 | carbon_filter_period_setpoint | carbon_filter_period_setpoint
ahu-24 | ahu-24_3 | hygroscopic_wheel_period_setpoint | hygroscopic_wheel_period_setpoint
ahu-24 | ahu-24_3 | exhaust_fan_offset_percentage_setpoint | exhaust_fan_offset_percentage_setpoint
ahu-24 | ahu-24_3 | heating_water_valve_demand_percentage_setpoint | heating_water_valve_demand_percentage_setpoint
ahu-24 | ahu-24_3 | chilled_water_valve_demand_percentage_setpoint | chilled_water_valve_demand_percentage_setpoint
ahu-24 | vsd-sf1 | supply_air_damper_percentage_sensor | supply_air_damper_percentage_sensor
ahu-24 | vsd-sf1 | mixing_air_damper_percentage_sensor | mixing_air_damper_percentage_sensor
ahu-24 | vsd-sf1 | supply_air_damper_percentage_command | supply_air_damper_percentage_command
ahu-24 | vsd-sf1 | mixing_air_damper_percentage_command | mixing_air_damper_percentage_command
ahu-24 | vsd-sf1 | supply_panel_filter_differential_pressure_sensor | supply_panel_filter_differential_pressure_sensor
ahu-24 | vsd-sf1 | supply_air_pressure_sensor | supply_air_pressure_sensor
ahu-24 | vsd-sf1 | supply_fan_run_status | supply_fan_run_status
ahu-24 | vsd-sf1 | supply_fan_fault_status | supply_fan_fault_status
ahu-24 | vsd-sf1 | supply_air_high_pressure_status | supply_air_high_pressure_status
ahu-24 | vsd-sf1 | supply_fan_speed_frequency_sensor | supply_fan_speed_frequency_sensor
ahu-24 | vsd-sf1 | supply_fan_alarm_status | supply_fan_alarm_status
ahu-24 | vsd-sf1 | supply_fan_auto_status | supply_fan_auto_status
ahu-24 | vsd-sf1 | supply_fan_power_sensor | supply_fan_power_sensor
ahu-24 | vsd-sf1 | supply_fan_energy_sensor | supply_fan_energy_sensor
ahu-24 | vsd-sf1 | supply_fan_current_sensor | supply_fan_current_sensor
ahu-24 | vsd-sf1 | supply_fan_voltage_sensor | supply_fan_voltage_sensor
ahu-24 | vsd-sf1 | supply_fan_run_period_sensor | supply_fan_run_period_sensor
ahu-24 | vsd-sf1 | supply_air_high_pressure_setpoint | supply_air_high_pressure_setpoint
ahu-24 | vsd-sf1 | supply_air_pressure_setpoint | supply_air_pressure_setpoint
ahu-24 | vsd-ef1 | exhaust_air_damper_percentage_sensor | exhaust_air_damper_percentage_sensor
ahu-24 | vsd-ef1 | exhaust_air_damper_percentage_command | exhaust_air_damper_percentage_command
ahu-24 | vsd-ef1 | exhaust_panel_filter_differential_pressure_sensor | exhaust_panel_filter_differential_pressure_sensor
ahu-24 | vsd-ef1 | supply_bag_filter_differential_pressure_sensor | supply_bag_filter_differential_pressure_sensor
ahu-24 | vsd-ef1 | exhaust_air_pressure_sensor | exhaust_air_pressure_sensor
ahu-24 | vsd-ef1 | exhaust_fan_run_status | exhaust_fan_run_status
ahu-24 | vsd-ef1 | exhaust_fan_fault_status | exhaust_fan_fault_status
ahu-24 | vsd-ef1 | exhaust_air_low_pressure_status | exhaust_air_low_pressure_status
ahu-24 | vsd-ef1 | exhaust_fan_speed_frequency_sensor | exhaust_fan_speed_frequency_sensor
ahu-24 | vsd-ef1 | exhaust_fan_alarm_status | exhaust_fan_alarm_status
ahu-24 | vsd-ef1 | exhaust_fan_auto_status | exhaust_fan_auto_status
ahu-24 | vsd-ef1 | exhaust_fan_power_sensor | exhaust_fan_power_sensor
ahu-24 | vsd-ef1 | exhaust_fan_energy_sensor | exhaust_fan_energy_sensor
ahu-24 | vsd-ef1 | exhaust_fan_current_sensor | exhaust_fan_current_sensor
ahu-24 | vsd-ef1 | exhaust_fan_voltage_sensor | exhaust_fan_voltage_sensor
ahu-24 | vsd-ef1 | exhaust_fan_run_period_sensor | exhaust_fan_run_period_sensor
ahu-24 | vsd-ef1 | exhaust_air_low_pressure_setpoint | exhaust_air_low_pressure_setpoint
dmp-ahu-ea-1 | ahu-24_2 | exhaust_air_damper_percentage_sensor_1 | exhaust_air_damper_percentage_sensor | EDPM
dmp-ahu-ea-1 | ahu-24_2 | exhaust_air_damper_percentage_command_1 | exhaust_air_damper_percentage_command | EDPM
dmp-ahu-ea-2 | ahu-24_2 | exhaust_air_damper_percentage_sensor_2 | exhaust_air_damper_percentage_sensor | EDPM
dmp-ahu-ea-2 | ahu-24_2 | exhaust_air_damper_percentage_command_2 | exhaust_air_damper_percentage_command | EDPM
dmp-ahu-sa-1 | ahu-24_2 | supply_air_damper_percentage_sensor_1 | supply_air_damper_percentage_sensor | PDSCV
dmp-ahu-sa-1 | ahu-24_2 | supply_air_damper_percentage_command_1 | supply_air_damper_percentage_command | PDSCV
dmp-ahu-sa-2 | ahu-24_2 | supply_air_damper_percentage_sensor_2 | supply_air_damper_percentage_sensor | PDSCV
dmp-ahu-sa-2 | ahu-24_2 | supply_air_damper_percentage_command_2 | supply_air_damper_percentage_command | PDSCV
mtr-ahu-cw | ahu-24_1 | chilled_water_flowrate_sensor | chilled_water_flowrate_sensor
mtr-ahu-cw | ahu-24_1 | cooling_coil_energy_sensor | cooling_coil_energy_sensor
mtr-ahu-hw | ahu-24_1 | heating_water_flowrate_sensor | heating_water_flowrate_sensor
mtr-ahu-hw | ahu-24_1 | heating_coil_energy_sensor | heating_coil_energy_sensor
ahu-11 | ahu-11_1 | supply_air_temperature_sensor | supply_air_temperature_sensor | STM | Existing
ahu-11 | ahu-11_1 | zone_air_temperature_sensor | zone_air_temperature_sensor | ZTM, ZTC, CHWZTC | Existing
ahu-11 | ahu-11_1 | fire_alarm_status | fire_alarm_status |  | New Field & Abstract Required
ahu-11 | ahu-11_1 | chilled_water_valve_percentage_command | chilled_water_valve_percentage_command | CHWZTC | Existing
ahu-11 | ahu-11_1 | chilled_water_flowrate_sensor | chilled_water_flowrate_sensor | CHWFRM | Existing
ahu-11 | ahu-11_1 | entering_cooling_coil_temperature_sensor | entering_cooling_coil_temperature_sensor |  | New Field & Abstract Required
ahu-11 | ahu-11_1 | leaving_cooling_coil_temperature_sensor | leaving_cooling_coil_temperature_sensor | CHWZTC | Existing
ahu-11 | ahu-11_1 | cooling_coil_differential_temperature_sensor | cooling_coil_differential_temperature_sensor |  | New Field & Abstract Required
ahu-11 | ahu-11_1 | cooling_coil_energy_sensor | cooling_coil_energy_sensor |  | New Abstract Required
ahu-11 | ahu-11_1 | zone_air_pid_integral_temperature_setpoint | zone_air_pid_integral_temperature_setpoint |  | New Subfields, Field & Abstract Required
ahu-11 | ahu-11_1 | zone_air_pid_derivative_temperature_setpoint | zone_air_pid_derivative_temperature_setpoint |  | New Subfields, Field & Abstract Required
ahu-11 | ahu-11_1 | zone_air_temperature_setpoint | zone_air_temperature_setpoint | ZTC, CHWZTC | Existing
ahu-11 | ahu-11_2 | supply_air_damper_alarm_status | supply_air_damper_alarm_status |  | New Field & Abstract Required
ahu-11 | ahu-11_2 | supply_air_volume_sensor | supply_air_volume_sensor |  | New Field & Abstract Required
ahu-11 | ahu-11_2 | supply_fan_demand_status | supply_fan_demand_status |  | New Subfield, Field & Abstract Required
ahu-11 | ahu-11_2 | zone_air_pid_gain_temperature_setpoint | zone_air_pid_gain_temperature_setpoint |  | New Subfields, Field & Abstract Required
ahu-11 | ahu-11_2 | exhaust_fan_offset_percentage_setpoint | exhaust_fan_offset_percentage_setpoint |  | New Subfield, Field & Abstract Required
ahu-11 | ahu-11_2 | chilled_water_valve_demand_percentage_setpoint | chilled_water_valve_demand_percentage_setpoint |  | New Subfield, Field & Abstract Required
ahu-11 | vsd-sf2 | supply_air_damper_percentage_sensor | supply_air_damper_percentage_sensor | PDSCV
ahu-11 | vsd-sf2 | supply_air_damper_percentage_command | supply_air_damper_percentage_command | PDSCV
ahu-11 | vsd-sf2 | safety_interlock | safety_interlock |  | New Subfield, Field & Abstract Required
ahu-11 | vsd-sf2 | supply_bag_filter_differential_pressure_sensor | supply_bag_filter_differential_pressure_sensor |  | New Subfield, Field & Abstract Required
ahu-11 | vsd-sf2 | supply_air_pressure_sensor | supply_air_pressure_sensor |  | New Field & Abstract Required
ahu-11 | vsd-sf2 | supply_fan_run_status | supply_fan_run_status
ahu-11 | vsd-sf2 | supply_fan_fault_status | supply_fan_fault_status
ahu-11 | vsd-sf2 | supply_air_high_pressure_status | supply_air_high_pressure_status
ahu-11 | vsd-sf2 | supply_fan_speed_frequency_sensor | supply_fan_speed_frequency_sensor
ahu-11 | vsd-sf2 | supply_fan_alarm_status | supply_fan_alarm_status
ahu-11 | vsd-sf2 | supply_fan_auto_status | supply_fan_auto_status
ahu-11 | vsd-sf2 | supply_fan_power_sensor | supply_fan_power_sensor
ahu-11 | vsd-sf2 | supply_fan_energy_sensor | supply_fan_energy_sensor
ahu-11 | vsd-sf2 | supply_fan_current_sensor | supply_fan_current_sensor
ahu-11 | vsd-sf2 | supply_fan_voltage_sensor | supply_fan_voltage_sensor
ahu-11 | vsd-sf2 | supply_fan_run_period_sensor | supply_fan_run_period_sensor
ahu-11 | vsd-sf2 | drive_dc_voltage_sensor | drive_dc_voltage_sensor
ahu-11 | vsd-sf2 | thermal_overload_percentage_sensor | thermal_overload_percentage_sensor
ahu-11 | vsd-sf2 | thermal_overload_alarm_status | thermal_overload_alarm_status
ahu-11 | vsd-sf2 | heatsync_temperature_sensor | heatsync_temperature_sensor
ahu-11 | vsd-sf2 | supply_air_high_pressure_setpoint | supply_air_high_pressure_setpoint

## asset_template
entity_instance_name | udmi.system.location.site | udmi.pointset.points | udmi.system.location.section | udmi.system.location.position.x | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.cloud.auth_type | dbo.devices_or_virtual_devices | dbo.type | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | location | reporting_device