## Example Points Export Bayview
Location | Control Program | Name | Type | Object ID | Device ID | Object Name | Exp:Num | I/O Type | Path
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | AHU-3 Airlow Monitoring Station 1 ai | BAI | AI:6 | DEV:2522801 | ahu-3_airflow_monitoring_station_ai_3 | 0:2 | 0-20 mA | #b123_ahu3_local_manager/ahu-3_airflow_monitoring_station_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | AHU-3 CHWR Temperature ai | BAI | AI:36 | DEV:2522801 | ahu-3_chwr_temperature_ai_3 | 2:15 | Thermistor | #b123_ahu3_local_manager/ahu-3_chwr_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | AHU-3 Duct Static Pressure 1 ai | BAI | AI:15 | DEV:2522801 | ahu-3_duct_static_pressure_1_ai_3 | 0:1 | 0-20 mA | #b123_ahu3_local_manager/ahu-3_duct_static_pressure_1_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | AHU-3 Duct Static Pressure 2 ai | BAI | AI:16 | DEV:2522801 | ahu-3_duct_static_pressure_2_ai_3 | 2:6 | 0-20 mA | #b123_ahu3_local_manager/ahu-3_duct_static_pressure_2_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Supply Air Temperature 01 ai | BAI | AI:41 | DEV:2522801 | supply_air_temperature_01_ai_3 | 0:5 | Thermistor | #b123_ahu3_local_manager/supply_air_temperature_01_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Supply Air Temperature 02 ai | BAI | AI:42 | DEV:2522801 | supply_air_temperature_02_ai_3 | 1:3 | Thermistor | #b123_ahu3_local_manager/supply_air_temperature_02_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Supply Air Temperature 03 ai | BAI | AI:43 | DEV:2522801 | supply_air_temperature_03_ai_3 | 1:13 | Thermistor | #b123_ahu3_local_manager/supply_air_temperature_03_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Supply Air Temperature 04 ai | BAI | AI:32 | DEV:2522801 | supply_air_temperature_04_ai_3 | 2:16 | Thermistor | #b123_ahu3_local_manager/supply_air_temperature_04_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Supply Air Temperature 05 ai | BAI | AI:44 | DEV:2522801 | supply_air_temperature_05_ai_3 | 3:1 | Thermistor | #b123_ahu3_local_manager/supply_air_temperature_05_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | Emergency Egress Push Button bi | BBI | BI:7 | DEV:2522801 | emergency_egress_push_button_bi_3 | 3:12 | Dry Contact | #b123_ahu3_local_manager/emergency_egress_push_button_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-07 Closed Status bi | BBI | BI:18 | DEV:2522801 | fsd-031-07_closed_status_bi_3 | 2:7 | Dry Contact | #b123_ahu3_local_manager/fsd-031-07_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-08 Closed Status bi | BBI | BI:19 | DEV:2522801 | fsd-031-08_closed_status_bi_3 | 2:8 | Dry Contact | #b123_ahu3_local_manager/fsd-031-08_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-09 Closed Status bi | BBI | BI:20 | DEV:2522801 | fsd-031-09_closed_status_bi_3 | 2:9 | Dry Contact | #b123_ahu3_local_manager/fsd-031-09_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-10 Closed Status bi | BBI | BI:21 | DEV:2522801 | fsd-031-10_closed_status_bi_3 | 2:10 | Dry Contact | #b123_ahu3_local_manager/fsd-031-10_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-11 Closed Status bi | BBI | BI:22 | DEV:2522801 | fsd-031-11_closed_status_bi_3 | 2:11 | Dry Contact | #b123_ahu3_local_manager/fsd-031-11_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-12 Closed Status bi | BBI | BI:23 | DEV:2522801 | fsd-031-12_closed_status_bi_3 | 2:12 | Dry Contact | #b123_ahu3_local_manager/fsd-031-12_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | FSD-031-13 Closed Status bi | BBI | BI:24 | DEV:2522801 | fsd-031-13_closed_status_bi_3 | 2:13 | Dry Contact | #b123_ahu3_local_manager/fsd-031-13_closed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3 Local Manager | High Pressure Status bi | BBI | BI:25 | DEV:2522801 | high_pressure_status_bi_3 | 2:14 | Dry Contact | #b123_ahu3_local_manager/high_pressure_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Return Air Temperature ai | BAI | AI:42 | DEV:2522801 | return_air_temperature_ai_4 | 0:5 | Thermistor | #b123_ahu3-1/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Supply Air Temperature 01 ai | BAI | AI:41 | DEV:2522801 | supply_air_temperature_01_ai_3 | 0:5 | Thermistor | #b123_ahu3-1/supply_air_temperature_01_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | CHW Control Valve Feedback ai | BAI | AI:19 | DEV:2522801 | chw_control_valve_feedback_ai_4 | 0:8 | 0-20 mA | #b123_ahu3-1/chw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Cooling Coil Air Temperature ai | BAI | AI:20 | DEV:2522801 | cooling_coil_air_temperature_ai_4 | 0:4 | Thermistor | #b123_ahu3-1/cooling_coil_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | HHW Control Valve Feedback ai | BAI | AI:22 | DEV:2522801 | hhw_control_valve_feedback_ai_4 | 0:9 | 0-20 mA | #b123_ahu3-1/hhw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Supply Fan VFD Feedback ai | BAI | AI:17 | DEV:2522801 | supply_fan_vfd_feedback_ai_4 | 0:10 | 0-20 mA | #b123_ahu3-1/supply_fan_vfd_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Outside Air Damper 1 Status ai | BBI | BI:9 | DEV:2522801 | outside_air_damper_1_status_ai_4 | 2:3 | Dry Contact | #b123_ahu3-1/outside_air_damper_1_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Outside Air Damper 2 Status ai | BBI | BI:10 | DEV:2522801 | outside_air_damper_2_status_ai_4 | 2:4 | Dry Contact | #b123_ahu3-1/outside_air_damper_2_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | CHW Control Valve Command ao | BAO | AO:8 | DEV:2522801 | chw_control_valve_command_ao_4 | 0:1 | Electrical 0-10 Volt | #b123_ahu3-1/chw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | HHW Control Valve Command ao | BAO | AO:9 | DEV:2522801 | hhw_control_valve_command_ao_4 | 0:2 | Electrical 0-10 Volt | #b123_ahu3-1/hhw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Outside Air Damper 1 Command ao | BAO | AO:10 | DEV:2522801 | outside_air_damper_1_command_ao_4 | 0:5 | Electrical 0-10 Volt | #b123_ahu3-1/outside_air_damper_1_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Outside Air Damper 2 Command ao | BAO | AO:6 | DEV:2522801 | outside_air_damper_2_command_ao_4 | 0:6 | Electrical 0-10 Volt | #b123_ahu3-1/outside_air_damper_2_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-1 | Supply Fan VFD Speed Command ao | BAO | AO:7 | DEV:2522801 | supply_fan_vfd_speed_command_ao_4 | 0:3 | Electrical 0-10 Volt | #b123_ahu3-1/supply_fan_vfd_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | CHW Control Valve Feedback ai | BAI | AI:23 | DEV:2522801 | chw_control_valve_feedback_ai_5 | 1:6 | 0-10 Volt | #b123_ahu3-2/chw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Cooling Coil Air Temperature ai | BAI | AI:26 | DEV:2522801 | cooling_coil_air_temperature_ai_5 | 1:2 | Thermistor | #b123_ahu3-2/cooling_coil_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | HHW Control Valve Feedback ai | BAI | AI:25 | DEV:2522801 | hhw_control_valve_feedback_ai_5 | 1:7 | 0-10 Volt | #b123_ahu3-2/hhw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Supply Fan VFD Feedback ai | BAI | AI:30 | DEV:2522801 | supply_fan_vfd_feedback_ai_5 | 1:8 | 0-20 mA | #b123_ahu3-2/supply_fan_vfd_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Outside Air Damper 1 Status ai | BBI | BI:12 | DEV:2522801 | outside_air_damper_1_status_ai_5 | 1:9 | Dry Contact | #b123_ahu3-2/outside_air_damper_1_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Outside Air Damper 2 Status ai | BBI | BI:13 | DEV:2522801 | outside_air_damper_2_status_ai_5 | 1:10 | Dry Contact | #b123_ahu3-2/outside_air_damper_2_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | CHW Control Valve Command ao | BAO | AO:11 | DEV:2522801 | chw_control_valve_command_ao_5 | 0:7 | Electrical 0-10 Volt | #b123_ahu3-2/chw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | HHW Control Valve Command ao | BAO | AO:12 | DEV:2522801 | hhw_control_valve_command_ao_5 | 0:8 | Electrical 0-10 Volt | #b123_ahu3-2/hhw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Outside Air Damper 1 Command ao | BAO | AO:13 | DEV:2522801 | outside_air_damper_1_command_ao_5 | 1:3 | Electrical 0-10 Volt | #b123_ahu3-2/outside_air_damper_1_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Outside Air Damper 2 Command ao | BAO | AO:14 | DEV:2522801 | outside_air_damper_2_command_ao_5 | 1:4 | Electrical 0-10 Volt | #b123_ahu3-2/outside_air_damper_2_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-2 | Supply Fan VFD Speed Command ao | BAO | AO:15 | DEV:2522801 | supply_fan_vfd_speed_command_ao_5 | 1:1 | Electrical 0-10 Volt | #b123_ahu3-2/supply_fan_vfd_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | CHW Control Valve Feedback ai | BAI | AI:28 | DEV:2522801 | chw_control_valve_feedback_ai_6 | 1:16 | 0-10 Volt | #b123_ahu3-3/chw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Cooling Coil Air Temperature ai | BAI | AI:33 | DEV:2522801 | cooling_coil_air_temperature_ai_6 | 1:12 | Thermistor | #b123_ahu3-3/cooling_coil_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | HHW Control Valve Feedback ai | BAI | AI:29 | DEV:2522801 | hhw_control_valve_feedback_ai_6 | 2:1 | 0-10 Volt | #b123_ahu3-3/hhw_control_valve_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Supply Fan VFD Feedback ai | BAI | AI:37 | DEV:2522801 | supply_fan_vfd_feedback_ai_6 | 2:2 | 0-20 mA | #b123_ahu3-3/supply_fan_vfd_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Outside Air Damper 1 Status ai | BBI | BI:15 | DEV:2522801 | outside_air_damper_1_status_ai_6 | 0:11 | Dry Contact | #b123_ahu3-3/outside_air_damper_1_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Outside Air Damper 2 Status ai | BBI | BI:16 | DEV:2522801 | outside_air_damper_2_status_ai_6 | 0:12 | Dry Contact | #b123_ahu3-3/outside_air_damper_2_status_ai
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | CHW Control Valve Command ao | BAO | AO:16 | DEV:2522801 | chw_control_valve_command_ao_6 | 1:5 | Electrical 0-10 Volt | #b123_ahu3-3/chw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | HHW Control Valve Command ao | BAO | AO:17 | DEV:2522801 | hhw_control_valve_command_ao_6 | 1:6 | Electrical 0-10 Volt | #b123_ahu3-3/hhw_control_valve_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Outside Air Damper 1 Command ao | BAO | AO:18 | DEV:2522801 | outside_air_damper_1_command_ao_6 | 2:1 | Electrical 0-10 Volt | #b123_ahu3-3/outside_air_damper_1_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Outside Air Damper 2 Command ao | BAO | AO:19 | DEV:2522801 | outside_air_damper_2_command_ao_6 | 2:2 | Electrical 0-10 Volt | #b123_ahu3-3/outside_air_damper_2_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/AHU-3 System | AHU-3-3 | Supply Fan VFD Speed Command ao | BAO | AO:20 | DEV:2522801 | supply_fan_vfd_speed_command_ao_6 | 1:7 | Electrical 0-10 Volt | #b123_ahu3-3/supply_fan_vfd_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-1 | Cooling Change Over Valve Status bi | BBI | BI:2 | DEV:2522901 | cooling_change_over_valve_status_bi_1 | 0:1 | Dry Contact | #b123_cov-31-1/cooling_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-1 | Heating Change Over Valve Status bi | BBI | BI:3 | DEV:2522901 | heating_change_over_valve_status_bi_1 | 0:2 | Dry Contact | #b123_cov-31-1/heating_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-1 | Cooling Change Over Valve Command bo | BBO | BO:1 | DEV:2522901 | cooling_change_over_valve_command_bo_1 | 0:1 | Relay / Triac Output | #b123_cov-31-1/cooling_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-1 | Heating Change Over Valve Command bo | BBO | BO:2 | DEV:2522901 | heating_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_cov-31-1/heating_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-2 | Cooling Change Over Valve Status bi | BBI | BI:1 | DEV:2523001 | cooling_change_over_valve_status_bi_1 | 0:1 | Dry Contact | #b123_cov-31-2/cooling_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-2 | Heating Change Over Valve Status bi | BBI | BI:2 | DEV:2523001 | heating_change_over_valve_status_bi_1 | 0:2 | Dry Contact | #b123_cov-31-2/heating_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-2 | Cooling Change Over Valve Command bo | BBO | BO:1 | DEV:2523001 | cooling_change_over_valve_command_bo_1 | 0:1 | Relay / Triac Output | #b123_cov-31-2/cooling_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-2 | Heating Change Over Valve Command bo | BBO | BO:2 | DEV:2523001 | heating_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_cov-31-2/heating_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-3 | Cooling Change Over Valve Status bi | BBI | BI:3 | DEV:2522801 | cooling_change_over_valve_status_bi_2 | 3:6 | Dry Contact | #b123_cov-31-3/cooling_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-3 | Heating Change Over Valve Status bi | BBI | BI:4 | DEV:2522801 | heating_change_over_valve_status_bi_2 | 3:7 | Dry Contact | #b123_cov-31-3/heating_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-3 | Cooling Change Over Valve Command bo | BBO | BO:1 | DEV:2522801 | cooling_change_over_valve_command_bo_2 | 2:5 | Relay / Triac Output | #b123_cov-31-3/cooling_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-3 | Heating Change Over Valve Command bo | BBO | BO:2 | DEV:2522801 | heating_change_over_valve_command_bo_2 | 2:6 | Relay / Triac Output | #b123_cov-31-3/heating_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-4 | Cooling Change Over Valve Status bi | BBI | BI:5 | DEV:2522801 | cooling_change_over_valve_status_bi_7 | 3:9 | 1 | #b123_cov-31-4/cooling_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-4 | Heating Change Over Valve Status bi | BBI | BI:6 | DEV:2522801 | heating_change_over_valve_status_bi_7 | 3:10 | 1 | #b123_cov-31-4/heating_change_over_valve_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-4 | Cooling Change Over Valve Command bo | BBO | BO:3 | DEV:2522801 | cooling_change_over_valve_command_bo_7 | 2:7 | Relay / Triac Output | #b123_cov-31-4/cooling_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 Change Over Valves | RZ COV-31-4 | Heating Change Over Valve Command bo | BBO | BO:4 | DEV:2522801 | heating_change_over_valve_command_bo_7 | 2:8 | Relay / Triac Output | #b123_cov-31-4/heating_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/G3 General Exhaust fans | EF-15 (General Exhaust) | EF-15 General Exhaust Airflow ai | BAI | AI:29 | DEV:2522501 | ef-15_general_exhaust_airflow_ai_4 | 1:11 | 0-20 mA | #b123_general_exhaust_fan-15/ef-15_general_exhaust_airflow_ai
/Google Building/B123 - 456 Street Address/Floor Number/G3 General Exhaust fans | EF-15 (General Exhaust) | EF-15 VFD Feedback ai | BAI | AI:25 | DEV:2522501 | ef-15_vfd_feedback_ai_4 | 1:7 | 0-20 mA | #b123_general_exhaust_fan-15/ef-15_vfd_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/G3 General Exhaust fans | EF-15 (General Exhaust) | EF-15 VFD Speed Command ao | BAO | AO:11 | DEV:2522501 | ef-15_vfd_speed_command_ao_4 | 2:1 | Electrical 0-10 Volt | #b123_general_exhaust_fan-15/ef-15_vfd_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/G3 General Exhaust fans | EF-15 (General Exhaust) | EF-15 VFD Start Stop bo | BBO | BO:12 | DEV:2522501 | ef-15_vfd_start_stop_bo_4 | 1:8 | Relay / Triac Output | #b123_general_exhaust_fan-15/ef-15_vfd_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Return Air Temperature ai | BAI | AI:1 | DEV:2526111 | return_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-0-31-017/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Supply Air Temperature ai | BAI | AI:2 | DEV:2526111 | supply_air_temperature_ai_1 | 0:1 | Thermistor | #b123_fcu-0-31-017/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526111 | zone_temperature_asvi_1 |  |  | #b123_fcu-0-31-017/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Fan Speed Status bi | BBI | BI:1 | DEV:2526111 | fan_speed_status_bi_1 | 0:3 | Dry Contact | #b123_fcu-0-31-017/fan_speed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2526111 | chilled_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-0-31-017/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | High Fan Speed Command bo | BBO | BO:1 | DEV:2526111 | high_fan_speed_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-0-31-017/high_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Low Fan Speed Command bo | BBO | BO:2 | DEV:2526111 | low_fan_speed_command_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-0-31-017/low_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-017 | Medium Fan Speed Command bo | BBO | BO:3 | DEV:2526111 | medium_fan_speed_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-0-31-017/medium_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Return Air Temperature ai | BAI | AI:1 | DEV:2526108 | return_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-0-31-018/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Supply Air Temperature ai | BAI | AI:2 | DEV:2526108 | supply_air_temperature_ai_1 | 0:1 | Thermistor | #b123_fcu-0-31-018/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526108 | zone_temperature_asvi_1 |  |  | #b123_fcu-0-31-018/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Fan Speed Status bi | BBI | BI:1 | DEV:2526108 | fan_speed_status_bi_1 | 0:3 | Dry Contact | #b123_fcu-0-31-018/fan_speed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2526108 | chilled_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-0-31-018/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | High Fan Speed Command bo | BBO | BO:1 | DEV:2526108 | high_fan_speed_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-0-31-018/high_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Low Fan Speed Command bo | BBO | BO:2 | DEV:2526108 | low_fan_speed_command_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-0-31-018/low_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-018 | Medium Fan Speed Command bo | BBO | BO:3 | DEV:2526108 | medium_fan_speed_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-0-31-018/medium_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Return Air Temperature ai | BAI | AI:1 | DEV:2526123 | return_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-0-31-021/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Supply Air Temperature ai | BAI | AI:2 | DEV:2526123 | supply_air_temperature_ai_1 | 0:1 | Thermistor | #b123_fcu-0-31-021/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526123 | zone_temperature_asvi_1 |  |  | #b123_fcu-0-31-021/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Fan Speed Status bi | BBI | BI:1 | DEV:2526123 | fan_speed_status_bi_1 | 0:3 | Dry Contact | #b123_fcu-0-31-021/fan_speed_status_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2526123 | chilled_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-0-31-021/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | High Fan Speed Command bo | BBO | BO:1 | DEV:2526123 | high_fan_speed_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-0-31-021/high_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Low Fan Speed Command bo | BBO | BO:2 | DEV:2526123 | low_fan_speed_command_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-0-31-021/low_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | FCU-0-31-021 | Medium Fan Speed Command bo | BBO | BO:3 | DEV:2526123 | medium_fan_speed_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-0-31-021/medium_fan_speed_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-079 | Airflow Control | BAF |  | DEV:2526107 |  |  |  | #b123_evav-0-31-079/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-079 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526107 | flow_input_1 | 0:1 | Flow Input | #b123_evav-0-31-079/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-080 | Airflow Control | BAF |  | DEV:2526106 |  |  |  | #b123_evav-0-31-080/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-080 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526106 | flow_input_1 | 0:1 | Flow Input | #b123_evav-0-31-080/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-081 | Airflow Control | BAF |  | DEV:2526121 |  |  |  | #b123_evav-0-31-081/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-081 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526121 | flow_input_1 | 0:1 | Flow Input | #b123_evav-0-31-081/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-082 | Airflow Control | BAF |  | DEV:2526120 |  |  |  | #b123_evav-0-31-082/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-082 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526120 | flow_input_1 | 0:1 | Flow Input | #b123_evav-0-31-082/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-083 | Airflow Control | BAF |  | DEV:2526122 |  |  |  | #b123_evav-0-31-083/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | EVAV-0-31-083 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526122 | flow_input_1 | 0:1 | Flow Input | #b123_evav-0-31-083/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-087 | Airflow Control | BAF |  | DEV:2526109 |  |  |  | #b123_vav-rh-0-31-087/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-087 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526109 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-087/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-087 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526109 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-087/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-087 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526109 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-087/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-087 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526109 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-087/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-088 | Airflow Control | BAF |  | DEV:2526110 |  |  |  | #b123_vav-rh-0-31-088/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-088 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526110 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-088/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-088 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526110 | discharge_air_temprature_ai_1 | 0:1 | 1 | #b123_vav-rh-0-31-088/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-088 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526110 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-088/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-088 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526110 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-088/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Airflow Control | BAF |  | DEV:2528722 |  |  |  | #b123_vav-rh-0-31-089_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528722 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-089_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528722 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-089_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528722 | zone_co2_asvi_1 |  |  | #b123_vav-rh-0-31-089_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Zone Humidity asvi | ASVI | AI:5 | DEV:2528722 | zone_humidity_asvi_1 |  |  | #b123_vav-rh-0-31-089_co2/zone_humidity_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528722 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-089_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528722 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-089_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-089 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528722 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-0-31-089_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Airflow Control | BAF |  | DEV:2528723 |  |  |  | #b123_vav-rh-0-31-090_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528723 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-090_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528723 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-090_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528723 | zone_co2_asvi_1 |  |  | #b123_vav-rh-0-31-090_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Zone Humidity asvi | ASVI | AI:5 | DEV:2528723 | zone_humidity_asvi_1 |  |  | #b123_vav-rh-0-31-090_co2/zone_humidity_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528723 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-090_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528723 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-090_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-090 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528723 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-0-31-090_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Airflow Control | BAF |  | DEV:2526102 |  |  |  | #b123_vav-rh-0-31-091_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526102 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-091_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526102 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-091_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2526102 | zone_co2_asvi_1 |  |  | #b123_vav-rh-0-31-091_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Zone Humidity asvi | ASVI | AI:5 | DEV:2526102 | zone_humidity_asvi_1 |  |  | #b123_vav-rh-0-31-091_co2/zone_humidity_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2526102 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-091_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Damper Control ao | BAO | AO:1 | DEV:2526102 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-091_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-091 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2526102 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-0-31-091_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Airflow Control | BAF |  | DEV:2526101 |  |  |  | #b123_vav-rh-0-31-092_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526101 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-092_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526101 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-092_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2526101 | zone_co2_asvi_1 |  |  | #b123_vav-rh-0-31-092_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2526101 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-092_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Damper Control ao | BAO | AO:1 | DEV:2526101 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-092_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-092 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2526101 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-0-31-092_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-093 | Airflow Control | BAF |  | DEV:2526105 |  |  |  | #b123_vav-rh-0-31-093/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-093 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526105 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-093/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-093 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526105 | discharge_air_temprature_ai_1 | 0:1 | 1 | #b123_vav-rh-0-31-093/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-093 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526105 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-093/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-093 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526105 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-093/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-094 | Airflow Control | BAF |  | DEV:2526104 |  |  |  | #b123_vav-rh-0-31-094/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-094 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526104 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-094/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-094 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526104 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-094/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-094 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526104 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-094/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-094 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526104 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-094/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-095 | Airflow Control | BAF |  | DEV:2526112 |  |  |  | #b123_vav-rh-0-31-095/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-095 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526112 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-095/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-095 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526112 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-095/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-095 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526112 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-095/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-095 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526112 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-095/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-096 | Airflow Control | BAF |  | DEV:2526117 |  |  |  | #b123_vav-rh-0-31-096/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-096 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526117 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-096/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-096 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526117 | discharge_air_temprature_ai_1 | 0:1 | 1 | #b123_vav-rh-0-31-096/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-096 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526117 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-096/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-096 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526117 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-096/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-097 | Airflow Control | BAF |  | DEV:2526119 |  |  |  | #b123_vav-rh-0-31-097/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-097 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526119 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-097/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-097 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526119 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-097/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-097 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526119 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-097/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-097 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526119 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-097/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Airflow Control | BAF |  | DEV:2526103 |  |  |  | #b123_vav-rh-0-31-098_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526103 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-098_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526103 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-098_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2526103 | zone_co2_asvi_1 |  |  | #b123_vav-rh-0-31-098_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2526103 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-098_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Damper Control ao | BAO | AO:1 | DEV:2526103 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-098_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-098 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2526103 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-0-31-098_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-099 | Airflow Control | BAF |  | DEV:2526118 |  |  |  | #b123_vav-rh-0-31-099/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-099 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526118 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-0-31-099/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-099 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526118 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-0-31-099/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-099 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526118 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-0-31-099/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 031 | VAV-RH-0-31-099 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2526118 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-0-31-099/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Fan Speed Feedback ai | BAI | AI:4 | DEV:2526116 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-1-31-020/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Return Air Temperature ai | BAI | AI:1 | DEV:2526116 | return_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-1-31-020/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Supply Air Temperature ai | BAI | AI:2 | DEV:2526116 | supply_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-1-31-020/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526116 | zone_temperature_asvi_1 |  |  | #b123_fcu-1-31-020/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2526116 | chilled_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-1-31-020/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Fan Speed Command ao | BAO | AO:2 | DEV:2526116 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-1-31-020/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | FCU-1-31-020 | Fan Start Stop bo | BBO | BO:1 | DEV:2526116 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-1-31-020/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | EVAV-1-31-063 | Airflow Control | BAF |  | DEV:2528725 |  |  |  | #b123_evav-1-31-063/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | EVAV-1-31-063 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528725 | flow_input_1 | 0:1 | Flow Input | #b123_evav-1-31-063/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | EVAV-1-31-063 | Zone Temperature asvi | ASVI | AI:2 | DEV:2528725 | zone_temperature_asvi_1 |  |  | #b123_evav-1-31-063/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | EVAV-1-31-064 | Airflow Control | BAF |  | DEV:2528724 |  |  |  | #b123_evav-1-31-064/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | EVAV-1-31-064 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528724 | flow_input_1 | 0:1 | Flow Input | #b123_evav-1-31-064/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Airflow Control | BAF |  | DEV:2526114 |  |  |  | #b123_vav-rh-1-31-026_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526114 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-1-31-026_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2526114 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-1-31-026_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2526114 | zone_co2_asvi_1 |  |  | #b123_vav-rh-1-31-026_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2526114 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-1-31-026_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Damper Control ao | BAO | AO:1 | DEV:2526114 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-1-31-026_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-RH-1-31-026 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2526114 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-1-31-026_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-304 CO2 | Airflow Control | BAF |  | DEV:2528726 |  |  |  | #b123_vav-co-1-31-304_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-304 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528726 | flow_input_1 | 0:1 | Flow Input | #b123_vav-co-1-31-304_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-304 CO2 | Zone CO2 asvi | ASVI | AI:2 | DEV:2528726 | zone_co2_asvi_1 |  |  | #b123_vav-co-1-31-304_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-304 CO2 | Zone Temperature asvi | ASVI | AI:3 | DEV:2528726 | zone_temperature_asvi_1 |  |  | #b123_vav-co-1-31-304_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-305 CO2 | Airflow Control | BAF |  | DEV:2528727 |  |  |  | #b123_vav-co-1-31-305_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-305 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528727 | flow_input_1 | 0:1 | Flow Input | #b123_vav-co-1-31-305_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-305 CO2 | Zone CO2 asvi | ASVI | AI:2 | DEV:2528727 | zone_co2_asvi_1 |  |  | #b123_vav-co-1-31-305_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-305 CO2 | Zone Temperature asvi | ASVI | AI:3 | DEV:2528727 | zone_temperature_asvi_1 |  |  | #b123_vav-co-1-31-305_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-307 CO2 | Airflow Control | BAF |  | DEV:2528729 |  |  |  | #b123_vav-co-1-31-307_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-307 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528729 | flow_input_1 | 0:1 | Flow Input | #b123_vav-co-1-31-307_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-307 CO2 | Zone CO2 asvi | ASVI | AI:2 | DEV:2528729 | zone_co2_asvi_1 |  |  | #b123_vav-co-1-31-307_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-307 CO2 | Zone Temperature asvi | ASVI | AI:3 | DEV:2528729 | zone_temperature_asvi_1 |  |  | #b123_vav-co-1-31-307_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-306 CO2 | Airflow Control | BAF |  | DEV:2526115 |  |  |  | #b123_vav-co-1-31-306_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-306 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2526115 | flow_input_1 | 0:1 | Flow Input | #b123_vav-co-1-31-306_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-306 CO2 | Zone CO2 asvi | ASVI | AI:2 | DEV:2526115 | zone_co2_asvi_1 |  |  | #b123_vav-co-1-31-306_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-306 CO2 | Zone Temperature asvi | ASVI | AI:3 | DEV:2526115 | zone_temperature_asvi_1 |  |  | #b123_vav-co-1-31-306_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-308 CO2 | Airflow Control | BAF |  | DEV:2528728 |  |  |  | #b123_vav-co-1-31-308_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-308 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528728 | flow_input_1 | 0:1 | Flow Input | #b123_vav-co-1-31-308_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-308 CO2 | Zone CO2 asvi | ASVI | AI:2 | DEV:2528728 | zone_co2_asvi_1 |  |  | #b123_vav-co-1-31-308_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Sector 131 | VAV-CO-1-31-308 CO2 | Zone Temperature asvi | ASVI | AI:3 | DEV:2528728 | zone_temperature_asvi_1 |  |  | #b123_vav-co-1-31-308_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Fan Speed Feedback ai | BAI | AI:1 | DEV:2528716 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-2-31-001/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Return Air Temperature ai | BAI | AI:2 | DEV:2528716 | return_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-2-31-001/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Supply Air Temperature ai | BAI | AI:3 | DEV:2528716 | supply_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-2-31-001/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528716 | zone_temperature_asvi_1 |  |  | #b123_fcu-2-31-001/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2528716 | chilled_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-2-31-001/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Fan Speed Command ao | BAO | AO:2 | DEV:2528716 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-2-31-001/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-001 | Fan Start Stop bo | BBO | BO:1 | DEV:2528716 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-2-31-001/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Fan Speed Feedback ai | BAI | AI:1 | DEV:2528701 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-2-31-004/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Return Air Temperature ai | BAI | AI:2 | DEV:2528701 | return_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-2-31-004/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Supply Air Temperature ai | BAI | AI:3 | DEV:2528701 | supply_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-2-31-004/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528701 | zone_temperature_asvi_1 |  |  | #b123_fcu-2-31-004/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | CHWS Change Over Valve Position bi | BBI | BI:1 | DEV:2528701 | chws_change_over_valve_position_bi_1 | 0:6 | Dry Contact | #b123_fcu-2-31-004/chws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | HWS Change Over Valve Position bi | BBI | BI:2 | DEV:2528701 | hws_change_over_valve_position_bi_1 | 0:5 | Dry Contact | #b123_fcu-2-31-004/hws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2528701 | chilled_water_valve_control_ao_1 | 0:3 | Electrical 0-10 Volt | #b123_fcu-2-31-004/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Fan Speed Command ao | BAO | AO:2 | DEV:2528701 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-2-31-004/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Hot Water Valve Control ao | BAO | AO:3 | DEV:2528701 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-2-31-004/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | CHWS Change Over Valve Command bo | BBO | BO:1 | DEV:2528701 | chws_change_over_valve_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-2-31-004/chws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | Fan Start Stop bo | BBO | BO:2 | DEV:2528701 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-2-31-004/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-004 | HWS Change Over Valve Command bo | BBO | BO:3 | DEV:2528701 | hws_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-2-31-004/hws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Fan Speed Feedback ai | BAI | AI:1 | DEV:2528703 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-2-31-005/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Return Air Temperature ai | BAI | AI:2 | DEV:2528703 | return_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-2-31-005/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Supply Air Temperature ai | BAI | AI:3 | DEV:2528703 | supply_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-2-31-005/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528703 | zone_temperature_asvi_1 |  |  | #b123_fcu-2-31-005/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | CHWS Change Over Valve Position bi | BBI | BI:1 | DEV:2528703 | chws_change_over_valve_position_bi_1 | 0:6 | Dry Contact | #b123_fcu-2-31-005/chws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | HWS Change Over Valve Position bi | BBI | BI:2 | DEV:2528703 | hws_change_over_valve_position_bi_1 | 0:5 | Dry Contact | #b123_fcu-2-31-005/hws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2528703 | chilled_water_valve_control_ao_1 | 0:3 | Electrical 0-10 Volt | #b123_fcu-2-31-005/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Fan Speed Command ao | BAO | AO:2 | DEV:2528703 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-2-31-005/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Hot Water Valve Control ao | BAO | AO:3 | DEV:2528703 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-2-31-005/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | CHWS Change Over Valve Command bo | BBO | BO:1 | DEV:2528703 | chws_change_over_valve_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-2-31-005/chws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | Fan Start Stop bo | BBO | BO:2 | DEV:2528703 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-2-31-005/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-005 | HWS Change Over Valve Command bo | BBO | BO:3 | DEV:2528703 | hws_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-2-31-005/hws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Fan Speed Feedback ai | BAI | AI:1 | DEV:2528721 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-2-31-006/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Return Air Temperature ai | BAI | AI:2 | DEV:2528721 | return_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-2-31-006/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Supply Air Temperature ai | BAI | AI:3 | DEV:2528721 | supply_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-2-31-006/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528721 | zone_temperature_asvi_1 |  |  | #b123_fcu-2-31-006/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | CHWS Change Over Valve Position bi | BBI | BI:1 | DEV:2528721 | chws_change_over_valve_position_bi_1 | 0:6 | Dry Contact | #b123_fcu-2-31-006/chws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | HWS Change Over Valve Position bi | BBI | BI:2 | DEV:2528721 | hws_change_over_valve_position_bi_1 | 0:5 | Dry Contact | #b123_fcu-2-31-006/hws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2528721 | chilled_water_valve_control_ao_1 | 0:3 | Electrical 0-10 Volt | #b123_fcu-2-31-006/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Fan Speed Command ao | BAO | AO:2 | DEV:2528721 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-2-31-006/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Hot Water Valve Control ao | BAO | AO:3 | DEV:2528721 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-2-31-006/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | CHWS Change Over Valve Command bo | BBO | BO:1 | DEV:2528721 | chws_change_over_valve_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-2-31-006/chws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | Fan Start Stop bo | BBO | BO:2 | DEV:2528721 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-2-31-006/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-006 | HWS Change Over Valve Command bo | BBO | BO:3 | DEV:2528721 | hws_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-2-31-006/hws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Fan Speed Feedback ai | BAI | AI:1 | DEV:2528710 | fan_speed_feedback_ai_1 | 0:1 | 0-5 Volt | #b123_fcu-2-31-007/fan_speed_feedback_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Return Air Temperature ai | BAI | AI:2 | DEV:2528710 | return_air_temperature_ai_1 | 0:3 | Thermistor | #b123_fcu-2-31-007/return_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Supply Air Temperature ai | BAI | AI:3 | DEV:2528710 | supply_air_temperature_ai_1 | 0:2 | Thermistor | #b123_fcu-2-31-007/supply_air_temperature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528710 | zone_temperature_asvi_1 |  |  | #b123_fcu-2-31-007/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | CHWS Change Over Valve Position bi | BBI | BI:1 | DEV:2528710 | chws_change_over_valve_position_bi_1 | 0:6 | Dry Contact | #b123_fcu-2-31-007/chws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | HWS Change Over Valve Position bi | BBI | BI:2 | DEV:2528710 | hws_change_over_valve_position_bi_1 | 0:5 | Dry Contact | #b123_fcu-2-31-007/hws_change_over_valve_position_bi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Chilled Water Valve Control ao | BAO | AO:1 | DEV:2528710 | chilled_water_valve_control_ao_1 | 0:3 | Electrical 0-10 Volt | #b123_fcu-2-31-007/chilled_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Fan Speed Command ao | BAO | AO:2 | DEV:2528710 | fan_speed_command_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_fcu-2-31-007/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Hot Water Valve Control ao | BAO | AO:3 | DEV:2528710 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_fcu-2-31-007/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | CHWS Change Over Valve Command bo | BBO | BO:1 | DEV:2528710 | chws_change_over_valve_command_bo_1 | 0:3 | Relay / Triac Output | #b123_fcu-2-31-007/chws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | Fan Start Stop bo | BBO | BO:2 | DEV:2528710 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_fcu-2-31-007/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | FCU-2-31-007 | HWS Change Over Valve Command bo | BBO | BO:3 | DEV:2528710 | hws_change_over_valve_command_bo_1 | 0:2 | Relay / Triac Output | #b123_fcu-2-31-007/hws_change_over_valve_command_bo
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-001 | Airflow Control | BAF |  | DEV:2528705 |  |  |  | #b123_evav-2-31-001/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-001 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528705 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-001/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-002 | Airflow Control | BAF |  | DEV:2528713 |  |  |  | #b265_bv_g2_evav-2-31-002/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-002 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528713 | flow_input_1 | 0:1 | Flow Input | #b265_bv_g2_evav-2-31-002/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-003 | Airflow Control | BAF |  | DEV:2528704 |  |  |  | #b265_bv_evav-2-31-003/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-003 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528704 | flow_input_1 | 0:1 | Flow Input | #b265_bv_evav-2-31-003/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-003 | Damper Control ao | BAO | AO:1 | DEV:2528704 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b265_bv_evav-2-31-003/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-004 | Airflow Control | BAF |  | DEV:2528712 |  |  |  | #b123_evav-2-31-004/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-004 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528712 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-004/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-004 | Damper Control ao | BAO | AO:1 | DEV:2528712 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_evav-2-31-004/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-005 | Airflow Control | BAF |  | DEV:2528719 |  |  |  | #b123_evav-2-31-005/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-005 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528719 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-005/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-006 | Airflow Control | BAF |  | DEV:2528702 |  |  |  | #b265_bv_evav-2-31-006/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-006 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528702 | flow_input_1 | 0:1 | Flow Input | #b265_bv_evav-2-31-006/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-007 | Airflow Control | BAF |  | DEV:2528720 |  |  |  | #b123_evav-2-31-007/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-007 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528720 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-007/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-008 | Airflow Control | BAF |  | DEV:2528718 |  |  |  | #b123_evav-2-31-008/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-008 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528718 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-008/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-008 | Damper Control ao | BAO | AO:1 | DEV:2528718 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_evav-2-31-008/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-009 | Airflow Control | BAF |  | DEV:2528711 |  |  |  | #b123_evav-2-31-009/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | EVAV-2-31-009 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528711 | flow_input_1 | 0:1 | Flow Input | #b123_evav-2-31-009/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Airflow Control | BAF |  | DEV:2528706 |  |  |  | #b123_vav-rh-2-31-001_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528706 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-001_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528706 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-001_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528706 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-001_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528706 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-001_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528706 | damper_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-2-31-001_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-001 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528706 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-001_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Airflow Control | BAF |  | DEV:2528714 |  |  |  | #b123_vav-rh-2-31-002_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528714 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-002_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528714 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-002_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528714 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-002_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528714 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-002_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-002 CO2 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2528714 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-002_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Airflow Control | BAF |  | DEV:2528707 |  |  |  | #b123_vav-rh-2-31-003_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528707 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-003_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528707 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-003_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528707 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-003_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528707 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-003_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528707 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-003_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-003 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528707 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-2-31-003_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Airflow Control | BAF |  | DEV:2528708 |  |  |  | #b123_vav-rh-2-31-004_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528708 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-004_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528708 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-004_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528708 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-004_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528708 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-004_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528708 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-004_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-004 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528708 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-2-31-004_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Airflow Control | BAF |  | DEV:2528715 |  |  |  | #b123_vav-rh-2-31-005_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528715 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-005_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528715 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-005_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528715 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-005_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528715 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-005_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Damper Control ao | BAO | AO:1 | DEV:2528715 | damper_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-005_co2/damper_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-005 CO2 | Hot Water Valve Control ao | BAO | AO:2 | DEV:2528715 | hot_water_valve_control_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_vav-rh-2-31-005_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Airflow Control | BAF |  | DEV:2528717 |  |  |  | #b123_vav-rh-2-31-006_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528717 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-006_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528717 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-006_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528717 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-006_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528717 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-006_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-006 CO2 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2528717 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-006_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Airflow Control | BAF |  | DEV:2528709 |  |  |  | #b123_vav-rh-2-31-007_co2/airflow_control
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Airflow Control / Flow Input | BAI | AI:1 | DEV:2528709 | flow_input_1 | 0:1 | Flow Input | #b123_vav-rh-2-31-007_co2/airflow_control/flow_input
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Discharge Air Temprature ai | BAI | AI:2 | DEV:2528709 | discharge_air_temprature_ai_1 | 0:1 | Thermistor | #b123_vav-rh-2-31-007_co2/discharge_air_temprature_ai
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Zone CO2 asvi | ASVI | AI:3 | DEV:2528709 | zone_co2_asvi_1 |  |  | #b123_vav-rh-2-31-007_co2/zone_co2_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Zone Temperature asvi | ASVI | AI:4 | DEV:2528709 | zone_temperature_asvi_1 |  |  | #b123_vav-rh-2-31-007_co2/zone_temperature_asvi
/Google Building/B123 - 456 Street Address/Floor Number/Zones/Sector 231 | VAV-RH-2-31-007 CO2 | Hot Water Valve Control ao | BAO | AO:1 | DEV:2528709 | hot_water_valve_control_ao_1 | 0:1 | Electrical 0-10 Volt | #b123_vav-rh-2-31-007_co2/hot_water_valve_control_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-1 | Duct Static Pressure ai | BAI | AI:1 | DEV:2525201 | duct_static_pressure_ai_1 | 0:1 | 0-20 mA | #b123_general_exhaust_fan-3-1/duct_static_pressure_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-1 | Fan Feedback ai | BAI | AI:2 | DEV:2525201 | fan_feedback_ai_1 | 0:2 | 0-20 mA | #b123_general_exhaust_fan-3-1/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-1 | Fan Fault bi | BBI | BI:1 | DEV:2525201 | fan_fault_bi_1 | 0:3 | Dry Contact | #b123_general_exhaust_fan-3-1/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-1 | Fan Speed Command ao | BAO | AO:1 | DEV:2525201 | fan_speed_command_ao_1 | 0:2 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-1/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-1 | Fan Start Stop bo | BBO | BO:1 | DEV:2525201 | fan_start_stop_bo_1 | 0:1 | Relay / Triac Output | #b123_general_exhaust_fan-3-1/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-2 | Duct Static Pressure ai | BAI | AI:3 | DEV:2525201 | duct_static_pressure_ai_2 | 0:4 | 0-20 mA | #b123_general_exhaust_fan-3-2/duct_static_pressure_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-2 | Fan Feedback ai | BAI | AI:4 | DEV:2525201 | fan_feedback_ai_2 | 0:5 | 0-20 mA | #b123_general_exhaust_fan-3-2/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-2 | Fan Fault bi | BBI | BI:2 | DEV:2525201 | fan_fault_bi_2 | 0:6 | Dry Contact | #b123_general_exhaust_fan-3-2/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-2 | Fan Speed Command ao | BAO | AO:2 | DEV:2525201 | fan_speed_command_ao_2 | 0:4 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-2/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-2 | Fan Start Stop bo | BBO | BO:2 | DEV:2525201 | fan_start_stop_bo_2 | 0:3 | Relay / Triac Output | #b123_general_exhaust_fan-3-2/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-3 | Fan Airflow ai | BAI | AI:5 | DEV:2525201 | fan_airflow_ai_3 | 0:7 | 0-20 mA | #b123_general_exhaust_fan-3-3/fan_airflow_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-3 | Fan Feedback ai | BAI | AI:6 | DEV:2525201 | fan_feedback_ai_3 | 0:8 | 0-20 mA | #b123_general_exhaust_fan-3-3/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-3 | Fan Fault bi | BBI | BI:3 | DEV:2525201 | fan_fault_bi_3 | 0:9 | Dry Contact | #b123_general_exhaust_fan-3-3/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-3 | Fan Speed Command ao | BAO | AO:3 | DEV:2525201 | fan_speed_command_ao_3 | 0:6 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-3/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-3 | Fan Start Stop bo | BBO | BO:3 | DEV:2525201 | fan_start_stop_bo_3 | 0:5 | Relay / Triac Output | #b123_general_exhaust_fan-3-3/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-4 | Fan Airflow ai | BAI | AI:7 | DEV:2525201 | fan_airflow_ai_4 | 0:10 | 0-20 mA | #b123_general_exhaust_fan-3-4/fan_airflow_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-4 | Fan Feedback ai | BAI | AI:8 | DEV:2525201 | fan_feedback_ai_4 | 0:11 | 0-20 mA | #b123_general_exhaust_fan-3-4/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-4 | Fan Fault bi | BBI | BI:4 | DEV:2525201 | fan_fault_bi_4 | 0:12 | Dry Contact | #b123_general_exhaust_fan-3-4/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-4 | Fan Speed Command ao | BAO | AO:4 | DEV:2525201 | fan_speed_command_ao_4 | 0:8 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-4/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-4 | Fan Start Stop bo | BBO | BO:4 | DEV:2525201 | fan_start_stop_bo_4 | 0:7 | Relay / Triac Output | #b123_general_exhaust_fan-3-4/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-5 | Duct Static Pressure ai | BAI | AI:9 | DEV:2525201 | duct_static_pressure_ai_5 | 1:4 | 0-20 mA | #b123_general_exhaust_fan-3-5/duct_static_pressure_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-5 | Fan Feedback ai | BAI | AI:10 | DEV:2525201 | fan_feedback_ai_5 | 1:2 | 0-20 mA | #b123_general_exhaust_fan-3-5/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-5 | Fan Fault bi | BBI | BI:5 | DEV:2525201 | fan_fault_bi_5 | 1:3 | Dry Contact | #b123_general_exhaust_fan-3-5/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-5 | Fan Speed Command ao | BAO | AO:5 | DEV:2525201 | fan_speed_command_ao_5 | 1:2 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-5/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-5 | Fan Start Stop bo | BBO | BO:5 | DEV:2525201 | fan_start_stop_bo_5 | 1:1 | Relay / Triac Output | #b123_general_exhaust_fan-3-5/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-6 | Duct Static Pressure ai | BAI | AI:11 | DEV:2525201 | duct_static_pressure_ai_6 | 1:4 | 0-20 mA | #b123_general_exhaust_fan-3-6/duct_static_pressure_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-6 | Fan Feedback ai | BAI | AI:12 | DEV:2525201 | fan_feedback_ai_6 | 1:5 | 0-20 mA | #b123_general_exhaust_fan-3-6/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-6 | Fan Fault bi | BBI | BI:6 | DEV:2525201 | fan_fault_bi_6 | 1:6 | Dry Contact | #b123_general_exhaust_fan-3-6/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-6 | Fan Speed Command ao | BAO | AO:6 | DEV:2525201 | fan_speed_command_ao_6 | 1:4 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-6/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-6 | Fan Start Stop bo | BBO | BO:6 | DEV:2525201 | fan_start_stop_bo_6 | 1:3 | Relay / Triac Output | #b123_general_exhaust_fan-3-6/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-7 | Fan Airflow ai | BAI | AI:13 | DEV:2525201 | fan_airflow_ai_7 | 1:7 | 0-20 mA | #b123_general_exhaust_fan-3-7/fan_airflow_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-7 | Fan Feedback ai | BAI | AI:14 | DEV:2525201 | fan_feedback_ai_7 | 1:8 | 0-20 mA | #b123_general_exhaust_fan-3-7/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-7 | Fan Fault bi | BBI | BI:7 | DEV:2525201 | fan_fault_bi_7 | 1:9 | Dry Contact | #b123_general_exhaust_fan-3-7/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-7 | Fan Speed Command ao | BAO | AO:7 | DEV:2525201 | fan_speed_command_ao_7 | 1:6 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-7/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-7 | Fan Start Stop bo | BBO | BO:7 | DEV:2525201 | fan_start_stop_bo_7 | 1:5 | Relay / Triac Output | #b123_general_exhaust_fan-3-7/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-8 | Fan Airflow ai | BAI | AI:15 | DEV:2525201 | fan_airflow_ai_8 | 1:10 | 0-20 mA | #b123_general_exhaust_fan-3-8/fan_airflow_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-8 | Fan Feedback ai | BAI | AI:16 | DEV:2525201 | fan_feedback_ai_8 | 1:11 | 0-20 mA | #b123_general_exhaust_fan-3-8/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-8 | Fan Fault bi | BBI | BI:8 | DEV:2525201 | fan_fault_bi_8 | 1:12 | Dry Contact | #b123_general_exhaust_fan-3-8/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-8 | Fan Speed Command ao | BAO | AO:8 | DEV:2525201 | fan_speed_command_ao_8 | 1:8 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-8/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-8 | Fan Start Stop bo | BBO | BO:8 | DEV:2525201 | fan_start_stop_bo_8 | 1:7 | Relay / Triac Output | #b123_general_exhaust_fan-3-8/fan_start_stop_bo
/Google Building/B123 - 456 Street Address/Roof | General EF-3-9 | Fan Airflow ai | BAI | AI:17 | DEV:2525201 | fan_airflow_ai_9 | 1:13 | 0-20 mA | #b123_general_exhaust_fan-3-9/fan_airflow_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-9 | Fan Feedback ai | BAI | AI:18 | DEV:2525201 | fan_feedback_ai_9 | 1:14 | 0-20 mA | #b123_general_exhaust_fan-3-9/fan_feedback_ai
/Google Building/B123 - 456 Street Address/Roof | General EF-3-9 | Fan Fault bi | BBI | BI:9 | DEV:2525201 | fan_fault_bi_9 | 1:15 | Dry Contact | #b123_general_exhaust_fan-3-9/fan_fault_bi
/Google Building/B123 - 456 Street Address/Roof | General EF-3-9 | Fan Speed Command ao | BAO | AO:9 | DEV:2525201 | fan_speed_command_ao_9 | 2:2 | Electrical 0-10 Volt | #b123_general_exhaust_fan-3-9/fan_speed_command_ao
/Google Building/B123 - 456 Street Address/Roof | General EF-3-9 | Fan Start Stop bo | BBO | BO:9 | DEV:2525201 | fan_start_stop_bo_9 | 2:1 | Relay / Triac Output | #b123_general_exhaust_fan-3-9/fan_start_stop_bo